## Sheet1
Water Audit and Other Statistics Worksheet with Formulas |  |  | Water Audit and Other Statistics Example |  |  | Water Audit and Other Statistics Worksheet For Recording Values
1. Report actual metered values where possible. If water uses are not metered, estimate values for each line based on available information. Water entering distribution systsem must equal the sum of Sales (line 5), Authorized System Usage (line 12) and Water Losses (line 19). For assistance , see AWWA M36 Manual - Water Audits and Loss Control Programs. |  |  | 1. Report actual metered values where possible. If water uses are not metered, estimate values for each line based on available information. Water entering distribution systsem must equal the sum of Sales (line 5), Authorized System Usage (line 12) and Water Losses (line 19). For assistance , see AWWA M36 Manual - Water Audits and Loss Control Programs. |  |  | 1. Report actual metered values where possible. If water uses are not metered, estimate values for each line based on available information. Water entering distribution systsem must equal the sum of Sales (line 5), Authorized System Usage (line 12) and Water Losses (line 19). For assistance , see AWWA M36 Manual - Water Audits and Loss Control Programs.
2. For Gallons used in the treatment process (line 3), estimate water used in production including filter backwash, pumps and other utility uses before the point of entry to the distribution system. |  |  | 2. For Gallons used in the treatment process (line 3), estimate water used in production including filter backwash, pumps and other utility uses before the point of entry to the distribution system. |  |  | 2. For Gallons used in the treatment process (line 3), estimate water used in production including filter backwash, pumps and other utility uses before the point of entry to the distribution system.
3. For Gallons used for other system uses (line 11), report other unmetered water used for systemoperation and maintenance, water used for non-regulated sewer utility and all other unmetered usage that is known to occur and does not fall into on of the other categories listed under Water Usage |  |  | 3. For Gallons used for other system uses (line 11), report other unmetered water used for systemoperation and maintenance, water used for non-regulated sewer utility and all other unmetered usage that is known to occur and does not fall into on of the other categories listed under Water Usage |  |  | 3. For Gallons used for other system uses (line 11), report other unmetered water used for systemoperation and maintenance, water used for non-regulated sewer utility and all other unmetered usage that is known to occur and does not fall into on of the other categories listed under Water Usage
4. For Gallons unknown/not accounted for, estimate the volume of water losses due to other real or apparent losses, including customer meter inaccracies, data errors, and unknown volumes. Unknown/unaccounted for volumes should be minimun to the extent possible. |  |  | 4. For Gallons unknown/not accounted for, estimate the volume of water losses due to other real or apparent losses, including customer meter inaccracies, data errors, and unknown volumes. Unknown/unaccounted for volumes should be minimun to the extent possible. |  |  | 4. For Gallons unknown/not accounted for, estimate the volume of water losses due to other real or apparent losses, including customer meter inaccracies, data errors, and unknown volumes. Unknown/unaccounted for volumes should be minimun to the extent possible.
"Input" means utility enters a numerical value in thousands of gallons. |  | Line # | "Input" means utility enters a numerical value in thousands of gallons. |  | Line # | "Input" means utility enters a numerical value in thousands of gallons. |  | Line #
Water Audit Statistics | Gallons (000's) | 1 | Water Audit Statistics | Gallons (000's) | 1 | Water Audit Statistics | Gallons (000's) | 1
Source of Water Supply Statistics - Ttal Annual Pumpage (000's): Input |  | 2 | Source of Water Supply Statistics - Ttal Annual Pumpage (000's): Input | 1000000 | 2 | Source of Water Supply Statistics - Ttal Annual Pumpage (000's): Input |  | 2
Less: Gallons (000's) used in the treatment process: Input |  | 3 | Less: Gallons (000's) used in the treatment process: Input | 1000 | 3 | Less: Gallons (000's) used in the treatment process: Input |  | 3
Subtotal: Gallons (000's) entering distribution system: Line (2 -3) | 0 | 4 | Subtotal: Gallons (000's) entering distribution system: Line (2 -3) | 999000 | 4 | Subtotal: Gallons (000's) entering distribution system: Line (2 -3) | Calculated | 4
Less: Gallons (000's) Sold (Revenue Water): Input |  | 5 | Less: Gallons (000's) Sold (Revenue Water): Input | 899000 | 5 | Less: Gallons (000's) Sold (Revenue Water): Input |  | 5
Gallons (000's) entering the distribution system but not sold (Non-Revenue Water) (4-5) | 0 | 6 | Gallons (000's) entering the distribution system but not sold (Non-Revenue Water) (4-5) | 100000 | 6 | Gallons (000's) entering the distribution system but not sold (Non-Revenue Water) (4-5) | Calculated | 6
Authorized System Uses: |  | 7 | Authorized System Uses: |  | 7 | Authorized System Uses: | Blank | 7
Gallons (000's) used to flush mains: Input |  | 8 | Gallons (000's) used to flush mains: Input | 2000 | 8 | Gallons (000's) used to flush mains: Input |  | 8
Gallons (000's) used for fire protection: Input |  | 9 | Gallons (000's) used for fire protection: Input | 1000 | 9 | Gallons (000's) used for fire protection: Input |  | 9
Gallons (000's) used to prevent freezing of distribtuion system: Input |  | 10 | Gallons (000's) used to prevent freezing of distribtuion system: Input | 3000 | 10 | Gallons (000's) used to prevent freezing of distribtuion system: Input |  | 10
Gallons (000's) used for other system uses: Input |  | 11 | Gallons (000's) used for other system uses: Input | 0 | 11 | Gallons (000's) used for other system uses: Input |  | 11
Subtotal: Authorized System Uses: Line (8+9+10+11) | 0 | 12 | Subtotal: Authorized System Uses: Line (8+9+10+11) | 6000 | 12 | Subtotal: Authorized System Uses: Line (8+9+10+11) | Calculated | 12
Water Losses (Real and Apparent): |  | 13 | Water Losses (Real and Apparent): |  | 13 | Water Losses (Real and Apparent): | Blank | 13
Gallons (000's) lost due to main leaks or breaks: Input |  | 14 | Gallons (000's) lost due to main leaks or breaks: Input | 5000 | 14 | Gallons (000's) lost due to main leaks or breaks: Input |  | 14
Gallons (000's) lost due to service leaks or breaks: Input |  | 15 | Gallons (000's) lost due to service leaks or breaks: Input | 500 | 15 | Gallons (000's) lost due to service leaks or breaks: Input |  | 15
Gallons (000's) lost due to hydrant leaks, tank overflows and pressure reducting valves: |  | 16 | Gallons (000's) lost due to hydrant leaks, tank overflows and pressure reducting valves: | 300 | 16 | Gallons (000's) lost due to hydrant leaks, tank overflows and pressure reducting valves: |  | 16
Gallons (000's) for unauthorized usage such as vandalism and theft: Input |  | 17 | Gallons (000's) for unauthorized usage such as vandalism and theft: Input | 200 | 17 | Gallons (000's) for unauthorized usage such as vandalism and theft: Input |  | 17
Gallons (000's) unknown/not accounted for: Line (6-12-14-15-16-17) | 0 | 18 | Gallons (000's) unknown/not accounted for: Line (6-12-14-15-16-17) | 88000 | 18 | Gallons (000's) unknown/not accounted for: Line (6-12-14-15-16-17) | Calculated | 18
Subtotal Water Losses: Line (14+15+16+17+18) | 0 | 19 | Subtotal Water Losses: Line (14+15+16+17+18) | 94000 | 19 | Subtotal Water Losses: Line (14+15+16+17+18) | Calculated | 19
Percentage of water entering distribution system that is sold: Line Percent (5/4) | #DIV/0! | 20 | Percentage of water entering distribution system that is sold: Line Percent (5/4) | 89.99% | 20 | Percentage of water entering distribution system that is sold: Line Percent (5/4) | Calculated | 20
Percentage of water Real and Apparent Losses: Line Percent (19/4) | #DIV/0! | 21 | Percentage of water Real and Apparent Losses: Line Percent (19/4) | 9.409% | 21 | Percentage of water Real and Apparent Losses: Line Percent (19/4) | Calculated | 21
If water losses esceed 15%, indicate causes: |  | 22 | If water losses esceed 15%, indicate causes: |  | 22 | If water losses esceed 15%, indicate causes: |  | 22
|  | 23 |  |  | 23 |  |  | 23
|  | 24 |  |  | 24 |  |  | 24
If water losses esceed 15%, identify actions taken to reduce water loss: |  | 25 | If water losses esceed 15%, identify actions taken to reduce water loss: |  | 25 | If water losses esceed 15%, identify actions taken to reduce water loss: |  | 25
|  | 26 |  |  | 26 |  |  | 26
|  | 27 |  |  | 27 |  |  | 27